# 摘要

本设计是在对山东铝业35kV供电系统的负荷状况的调查的基础上进行的变电站供电方案设计。

本次设计有35kV、10kV两个电压等级，35kV有两回电源线，其中一回为主电源，另一回作为备用电源，35kV、10kV电气主接线均采纳单母线分段接线方式。依据各侧的短路电流计算及高压电气选择规程选择了电气设备，并进行校验，设计了电气总平面布置图、35kV侧和10kV侧配电装置图并对主电力变压器的型号进行了选择和校验。主变压器采纳一般双绕组变压器。35kV 采纳屋内配电装置，开关柜采纳中置式高压开关柜；柜内采纳真空断路器。10kV电气设备采纳中置式高压开关柜；柜内采纳真空断路器。对于二次系统，阐述了变压器的继电爱护和输电线路的电流爱护，并进行了纵联差动爱护的整定计算，还设计了防雷爱护和接地装置。最终对变电站的直流系统进行了设计。

通过本次设计，结合现状条件，在确保平安牢靠的前提下，采纳成熟技术，选用牢靠节能的设备，保障山东铝厂厂用电的牢靠性，给工厂的正常生产供应牢靠的电力供应。

关键词： 电气主接线,短路电流计算,动稳定,热稳定,防雷爱护

# Abstract

The design is in the Shandong Aluminum 35kV distribution system load of the investigation on the basis of the electricity substation program Design.

The design of 35 kV and 10 kV voltage levels 2, back to a two 35kV power line, a return to the main power supply, Another back as a standby power supply, 35kV and 10kV main electrical wiring is the single-bus Sub Connection. According to the schedule for the calculation of short-circuit current and high voltage electrical order to choose the option of electrical equipment, and calibration, General Electric design a layout map, Side 35kV and 10kV distribution side of the installation as well as the main electricity transformer model for the selection and calibration. Transformer use ordinary double-winding transformers. 35kV distribution devices used inside and switchgear used the home-Switchgear; accordingly vacuum breaker. 10kV electrical equipment used the home-Switchgear; accordingly vacuum breaker. For the second system, described the protection of transformers and transmission lines in current protection, and the longitudinal differential protection setting, also designed a lightning protection and grounding devices. Finally, the substation DC system design.

During this design, with the status quo, ensuring safety and reliability under the premise of using mature technology, The selection of a reliable energy-saving equipment, plant protection Shandong Aluminum electricity reliability, to the normal production factories provide a reliable supply of electricity.

Keywords: electrical wiring, Short-circuit current calculation, Dynamic stability, Thermal stability, Lightning Protection

# 目 录

摘 要	I

Abstract	II

目 录	III

第一章 引 言	1

1.1我国电力工业发展概况	1

1.2 我国与发达国家的差距	2

1.3变电站所址的选择	3

1.4 站区布置	3

其次章 电气主接线的设计	5

2.1主接线设计的基本要求	5

2.2 电气主接线的基本接线及适用范围	7

2.3 变电站与电网的连接	10

第三章 变压器的选择	11

3.1 主变压器选择的理论依据	11

3.2 主变压器的计算与选择	13

第四章 短路电流计算	15

4.1 短路电流与最大持续工作电流的计算	15

第五章 电气设备选择	19

5.1电气设备选择的一般原则	19

5.2 电气设备选择的技术条件	19

5.3 高压断路器的选择	21

5.4 高压隔离开关的选择	23

5.5 熔断器的选择	24

5.6 互感器的选择	25

5.7  35KV侧主要电气设备的选择	30

5.8  10KV侧主要电气设备的选择	33

第六章 变电站的继电爱护	37

6.1 电力系统中继电爱护的基本任务和基本要求	37

6.2电力系统中继电爱护的整定计算	37

6.3电力变压器的爱护	40

第七章 防雷与直流电源系统设计	45

7.1变电站及电力线路的防雷设计	45

7.2防雷装置的选择	46

7.3低压配电系统的接地型式、接地故障爱护	48

7.4 直流电源系统设计	49

结 论	52

参考文献	53

致 谢	54

以上内容仅为本文档的试下载部分，为可阅读页数的一半内容。如要下载或阅读全文，请访问：https://d.book118.com/288114057013006034