全厂接地

Whole Plant Grounding

# 施工作业指导书

# Construction Methodology

作业项目名称：全厂接地

Project name:Whole Plant Grounding

专业：电气

Specialty:Electrical

2020年01月30日

January    30,2020

施工作业指导书审批表

Constructionworkinstructionapprovalform

| 作业项目名 Jobname |  | 全厂接地 whole plant grounding |
| --- | --- | --- |
| 编号No |  |  |
| 编制 Prepared by |  | 签名signature 日期date: |
| 专业审核 Department reyiew |  | 签名signature日期date: |
| 项目审批 | 工程 engineering | 签名signature日期date: |
|  | 质量quality | 签名signature日期date: |
|  | 安监Safety supervision | 签名signature日期date: |
|  | 总工Chief Engineer | 签名signature日期date |

目录TableofContents

1、编制依据	2

1、Reference	1

2、概述	2

2、Summary	2

3、主要工程量	2

3、Mainworkquantity  	2

4、作业条件	2

4、Workcondition	2

5、作业方案	3

5、Work scheme	3

6、强制性条文执行内容	6

6、Content of compulsoryprovisions  of engineering  constructionstandards	6

7、安全文明施工保障措施及风险控制计划表	7

7、 Content  of compulsoryprovisions  of engineering  construction  standards	7

8、质量控制措施	11

8、Qualitycontrolmeasures	11

9、绿色施工措施	12

9、Green  Construction  measures 	11

10、应急保障措施	13

10、Emergencysupport  measures 	13

1、编制依据

1、Reference

1.1浙江设计院提供的本项目的相关图纸；

1.1Relevant drawings ofthis project provided by Zhejiang Design Institute

2、概述

2、Summary

本工程为：孟加拉国库尔纳330MW(200-300MW)   双燃料联合循环电站项目，施工内容 为库尔纳项目全厂接地装置安装。工作内容主要包括全厂接地导体敷设，接地极安装，导体、

接地极的焊接，及与各种电气设备、桥、支架、避雷针及钢结构的连接。

The  project  is:BangladeshKhulna   330MW(200-300MW)combined   cycle(duelfuel)powerplantproject,theconstructioncontentisthewholeplantgroundinginstallation.Theworkmainlyincludesthewholeplantgroundingconductorlaying,groundingpoleinstallation,conductor,groundelectrodewelding,andvarious  electrical  equipment,cabletray,support,etc.Theconnection

oflightning rod and steelstructure.

# 3、主要工程量

# 3、Mainworkquantity

| 序号 number | 名称 name | 型号规格 typespecification | 单位 unit | 备注 remarks |
| --- | --- | --- | --- | --- |
| 1 | 软铜绞线 Soft copperstrand | TRJ-200mm² | m | 11700 |
| 2 | 软铜绞线 Soft copperstrand | TRJ-120mm² | m | 1800 |
| 3 | 镀铜钢棒 Copper platedsteel bar | ①16 | root | 180 |
| 4 | 接地井 Earthingpit |  | set | 9 |
| 5 | 镀锌钢管 Galvanized steelpipe | φ40 | m | 760 |
| 6 | 人体静电消除桩 Charge eliminator |  | PCs | 7 |

# 4、作业条件

# 4、Workcondition

| 主要设备 具备条件 Major equipmen Qualified | 需要具备的条件 Necessary conditions | 备注 Remarks |
| --- | --- | --- |
| 预备安装条件 Installation preparation Work | 场地、力能：场地平整，临时电源布置到现场，满足接地施工要求。 Site,force:flat site,temporary power tothesite,to meettherequirements of groundingconstruction |  |
|  | 环境：现场道路通畅，无上下交叉作业现象。 Environment:the road is smoothandthereisnocross-operation between topandbottom |  |
|  | 特殊工种：电焊工持有焊工资格证，已通过现场考试合格。 Special types of work:The welder holds thequalification certificate and passed theexamination |  |
| 工期 Construction period | 2020年03月11日至2021年05月10日 March11th 2020to May10th2021 |  |
| 人力 Manpower | Constructionmanager施工经理，1;Engineer工程师，1; Electrician电工，1;HSE engineer安全工程师，1;Electric welder焊工，1;Installer安装工5。Total合计，10。 |  |
| 机械 Machinery | 运输车1辆； ltransportvehicle; |  |
| 工器具 Toolsand instruments | 无齿锯1台，手提砂轮机3台，手电钻2台，其它专用工具(工人自备) 1 toothless saw,3 hand-held grinders,2electricdrills,otherspecial-purposetools(self-provided by workers) |  |
| 材料 Consumables | 施工用的各种消耗材料已经提出计划并采购到货，现场安全设 施已到位，现场规划已经完成。 The Various consumables of theconstruction havebeenpropose plan and purchase arrival,on-site safety facilitieshave beenput in place,Site planning has been completed.(See Annex constructio materialslist' |  |

5、作业方案

5、Workscheme

5.1施工工序流程

## 5.1Construction process flow char

# 5.2施工工序卡

## 5.2 Construction process card

| 1.概述Summary:接地沟开挖、接地极安装、主接地线敷设、引上线敷设、放热焊接、回 填、引上线与设备连接 Ground trench excavation,grounding pole installation,main ground wirelaying,lead wirelaying, exothermic welding,backfill,lead wire and equipmentconnection |  |  |
| --- | --- | --- |
| 2.操作方法Operationmethod: |  |  |
| 序号及步骤名称 Serial numberand stepname | 主要作业方法和操作要求 Main operation methods and requirements | 工艺质量要求 Qualityrequirements |

| 接地沟开控 Groundtrench excavation | 依据设计图纸给出的接地软铜绞线 敷设的位置进行土方开挖。 The earthworkis excavatedaccordingto the positionoflayingsoftcopper strandsin thedesigndrawing | 深度不小于0.8米，距离建筑物外墙大于1.5米。地下一次接地干线不得通过土建基础，只应在基础下 面或侧面通过，并要求接地网与土 建基础底部的垂直距离不小于 600mm. The depthis notlessthan0.8 meter,and the distancefromtheouter wallof thebuildingismorethan1.5 meters.The earthing meshshould not crossthefoundationofstructure,it should belaid underthe foundation orattheflankofthe foundation,the distance between structure foundationandearthing mesh shouldnotbelessthan 600mm |
| --- | --- | --- |
| 接地极安装 Grounding pole installation | 开挖接地沟过程中可利用挖掘机将 接地极垂直压入沟内，或者用人工将 接地极砸入接地沟。 During the excavationoftheearthing ditch,the earthingpolecanbe pressed verticallyinto theditch by excavator,or theearthpolecanbe smashedinto thegroundditchby hand | 接地极顶端距接地沟内地面预留 约100mm距离 A distanceofabout100mmfromthe topoftheearthpoletothe ground |

| 主接地线敷设 Main ground wire laying | 将软铜绞线敷设于电缆沟内尽量拉 直。 Lay softcopperstrandsincable trenches asstraightlyaspossible | 敷设过程中铜绞线不允许拧死结， 过路段或穿越建筑物下侧时必须 穿保护管进行敷设。 Copper strandsare notallowedto twist duringlaying.Whencrossing the road orthroughthelowerside of the building,it musthavea protectivepipeforlaying. |
| --- | --- | --- |
| 引上线敷设 Wirelaying | 根据图纸设计的上引位置敷设上引 线。 According tothedrawingdesign ofthe upper connected positiontolay thewire. | 敷设过程中铜绞线不允许拧死结。 接地引上线伸出地面以上0.3m。 Copperstranded wire arenot allowed totwistduringlaying.Up connected from Mainearthingconductor reach0.3 metersabove theground. |
| 放热焊接 Exothermic welding | 焊接时焊接模具必须安装牢固，必 须将导体、接地极夹紧。如果出现无法夹紧的缝隙，可利用泥土将缝 隙堵平。 When welding,the welding mould must be firmlyinstalled.The conductorandthegroundingelectrode must be clamped.Ifthereisany crack thatcannotbeclamped,it canbeblockedbysoil. | 必须利用专用的焊接模具与焊药。Special welding mould andsolder must beused |

| 回填 backfill | 直接使用开挖时的土壤进行回填。 The soilisbackfilled withthe excavatedsoildirectly | 回填土中不应含有杂物，回填后要 夯实。 There shouldbenodebrisinthebackfill,and itshouldbetamped after backfilling |
| --- | --- | --- |

以上内容仅为本文档的试下载部分，为可阅读页数的一半内容。如要下载或阅读全文，请访问：https://d.book118.com/356201112021010043